BUILDING RISK/HAZARD REGISTER

SCHOOL: 			Comeragh Wilderness Academy

ADDRESS:	Boolabeg, Rathgormack, Co. Waterford.

DATE: 				30/8/22

Kilcullen

Community Centre

INTRODUCTION

This document has endeavoured to set out the following:

- Highlight key issues from a visual inspection

- Provide recommendations for improvement / compliance

Every establishment should have its own individual emergency response / evacuation procedure which should cover the following basic facts in relation to fire hazards:

- What to do if you discover a fire

- What to do when you hear the fire alarm

- Calling the Fire Service

- Evacuation

- Assembly

- Roll Call

The fire procedures should be made available to all staff and included in the induction of all new starters.  It is recommended that the fire procedures be made available to users of the facility in the form of evacuation procedures posted throughout the premises.

A summary of the evacuation procedures should also be made available to all contractors who are employed to carry out works within the building.

EVACUATION PROCEDURES FOR PEOPLE WITH SPECIAL NEEDS

Particular attention will need to be given to visitors, pupils and staff who have special needs including those with a disability.

The fire Services position is that the building management are required to have procedures in place to evacuate all people from a building independent of assistance from the brigade.

Any staff that feel that they or a member of the public / visitor may require assistance in the event of an evacuation must inform the management in order for suitable arrangements to be put in place. There may be a need to adopt alternative procedures if they cannot be evacuated with the majority.  This may be as a result of particular mobility or sensory problems or because of the nature of the building(s) which makes it difficult to evacuate quickly - e.g. multi-storey blocks, forest etc.

A personal emergency evacuation plan (PEEP) may need to be developed for disabled persons who frequently use a building or have the potential to use the building.

When formulating a Personal Emergency Evacuation Plan consideration should be given to:

- The problems the individual may ensue if they encounter an evacuation

- What areas of the premises are most commonly used by the individual

- Location of safe refuges, (a relatively safe waiting area for short periods, which is separated from the fire by fire resisting construction and which has access to a final fire exit via a safe route).

- Identifying members of staff with designated responsibility for helping the evacuation of those persons requiring assistance, including staying with them in the safe refuge.  These individuals should be trained, easily identifiable, accessible and available at all times.

- Is the means of raising the alarm appropriate for the disability (e.g. hearing impairments)

- The current evacuation procedures (are they familiar to all staff and well-practised? Is extra training required in use of specialist equipment etc?)

## General Fire Precautions

All staff members and students should familiarise themselves as soon as possible with:

1.	The layout of the premises.

2.	The location and operation of emergency exits.

3.	The location and operation of extinguishers, hose reels and break glass units where fitted.

4.	The correct action to be taken on discovering a fire or if the alarm is sounded by somebody else.

EACH MEMBER OF STAFF AND STUDENTS SHOULD OBSERVE THE FOLLOWING RULES:

- Refuse / waste to be disposed of only at points intended for the purpose.

- Always discard your cigarette safely (i.e. in an appropriate metal bin) in a designated smoking area, denoted by signage, and positioned so as to ensure it is not in close proximity to any potential combustible sources.

- Smouldering material to be extinguished before disposal.

- Escape routes, extinguishers, and emergency exits to be kept clear at all times.

- Fire Doors and Smoke Doors must never be fixed in an open position.

- Faults in Electrical, Gas, Extinguishers, and Fire Alarm Equipment to be reported to Management.

- NO SMOKING or Naked Lights where Smoking is forbidden.

- Except with Management permission, no work to be done involving any Fire Hazard.

- Never use Fire Equipment for other uses besides Fire Fighting.

- NEVER smoke near gas cylinders, petrol, or other flammable substances.

- NEVER direct water at any electrical installation, equipment, or wiring.

| FIRE RISK |  | FIRE EXTINGUISHER COLOUR CODES |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | WATER |  |  | FOAM | CARBON DIOXIDE |  | DRY POWDER |  |
| #### Label Colour |  | Signal RED | Pale CREAM |  |  | BLACK |  | French BLUE |  |
| Paper, Wood, Textile & Fabric. |  |  |  |  |  |  |  |  |  |
| Flammable Liquids. |  |  |  |  |  |  |  |  |  |
| Flammable Gases. |  |  |  |  |  |  |  |  |  |
| Electrical Hazards. |  |  |  |  |  |  |  |  |  |
| Vehicle Protection. |  |  |  |  |  |  |  |  |  |

## Fire Fighting Equipment

Fire Fighting Equipment may be selected as per the table below:

Ensure all firefighting equipment is tested periodically by a competent person(s) and stored safely and their locations known to staff.

Ensure all applicable staff is trained in the use of firefighting equipment, and on fire procedures to ensure they do not put themselves in harm’s way.

IT IS RECOMMENDED DRAWINGS BE DRAFTED UPSHOWING

ESSENTIAL FIRE EQUIPMENT, FIRST AID EQUIPMENT,

EVACUATION POINTS AND ASSEMBLY POINT ETC.

Comeragh Wilderness Academy

GENERAL EMERGENCY PROCEDURES

FIRE EVACUATION

IF YOU FIND A FIRE OR ONE IS REPORTED TO YOU:

- Staff discovering a fire or other emergency for which the buildings should be evacuated should activate the alarm using the nearest available break glass call point. They should then notify fire Services and/or ambulance services of the exact location of the incident as per the emergency procedures.

Fire Fighting

- The safe evacuation of persons is an absolute priority. Staff may only attempt to deal with small fires, if it is safe to do so without putting themselves at risk, using portable firefighting equipment.

- Ensure the alarm is raised BEFORE attempting to tackle a fire.

NB. Staff should be made aware of the type and location of portable firefighting equipment and receive basic instruction in its correct use.

ON HEARING THE FIRE ALARM:

- All staff, visitors, occupants of building must respond to alarm activations.

- The fire alarm is a beeping sound when activated.

- When the alarm is activated an appointed fire warden or other appointed competent person(s) will check the fire panel and, if safe to do so, go to the zone where the alarm has been activated to investigate if there is a fire or false alarm.

- The appointed competent person(s) will summon the emergency services (DIAL 999) as necessary;

- Staff will supervise / affect the evacuation of visitors to the designated assembly point(s).

- Staff, visitors and contractors must leave the building by the nearest exit and report directly to the assembly point.

The fire assembly points need to be designated and the location made known to all employees and students, also the location should be described within the Safety Statement and on all Fire Orders. It is recommended that a visitor/contractor sign in log be made part of the emergency fire procedure to ensure all visitors/contractors are accounted for.

A Calm orderly exit is essential

Walk quickly – DO NOT RUN or stop to collect belongings

- On arrival at the assembly point a role call will take place to ensure all staff are present.

- Staff member of the School will take out Visitor/Contractor log etc. to the assembly point. The result of this check must be reported to the senior member of staff as soon as it is completed and/or emergency services.

- The senior member of staff will liaise with the Fire Services on their arrival.

- The building must not be re-entered until staff are notified it is safe to do so by the Fire Services/ senior member of staff.

- If the building cannot be reoccupied following an evacuation, staff will be allowed to go home but only by a senior member of staff and / or emergency services.

GENERAL EVACUATION FOR PEOPLE WITH SPECIAL NEEDS

Mobility Impairment

Those people who require only limited assistance should evacuate the building using the nearest exit. If they have to move at a slower pace they should allow other persons to exit the building before them and then continue their evacuation to a place of safety. A responsible member of staff / buddy system will be nominated to escort those who need assistance from the building.

Visual disability

People with a visual disability will usually require the assistance of one person, on stairways the helper should descend first with the person’s hand on their shoulder, on level surfaces they should take the helpers arm and follow them.

Hearing disability

People with a hearing disability should be escorted out of the building by staff.

In the event of staff with a hearing impairment joining then they may require additional means of being warned in the event of an alarm e.g. pager that vibrates when alarm is activated, flashing beacon linked to alarm etc.

Gas Leaks

If you smell gas, or suspect there is a gas escape, you should immediately:

- Open all doors and windows.

- Notify the senior member of staff of the incident.

- Check that all gas appliances are switched off.

- Shut off the gas supply at the meter control valve.

- Evacuate part or all of the premises as necessary.

- If gas continues to escape, telephone Bord Gais Emergency Number1850 20 50 50.

Chemical Spills

If it is safe to do so identify the substance spilled and take necessary action to minimise contamination if trained to do so.

It may be necessary to evacuate the room and ensure windows are opened.

If spill is severe, evacuate part or all of the building, using fire drill procedures if necessary.

Move all persons to a safe location and call the emergency services. The Fire & Rescue Service are the lead agency in dealing with chemical / toxic / hazardous spillage incidents.

If severe spill is immediately outside the building i.e. petrol, oil etc:

- Follow procedures to contain all persons within the building.

- Ensure all doors and windows are locked.

- Switch off fans or air conditioning

- Avoid using electrical equipment in case sparks are produced.

- Do not smoke.

FIRE DRILL RECORDS

In reference to Technical Guidance Document B 2006, section 1.3.6.5 Use of space within protected stairways – ‘A protected stairway needs to be relatively free of potential sources of fire’.

In accordance with General Application Regulations, part 2 Chapter 1, section 12 – Emergency Routes and exits - (a) emergency routes to emergency exits and the exits themselves are kept clear at all times and lead as directly as possible to the open air or to a safe area.

Technical Guidance Document B 2006, section 1.4.3.4 Amount of opening and effect on associated escape routes – All doors on escape routes should be hung to open not less than 90 degrees.

Technical Guidance Documents Appendix B, ‘All fire doors should be fitted with an automatic self-closing device which is capable of closing the door from any angle and against any latch fitted to the door’.

Section 1.4.8.5 Emergency escape lighting should be designed and installed in accordance with the relevant recommendations in I.S. 3217: 1989 Code of practice for emergency lighting.

Other Observed Issues:

- Add in any issues observed during site inspection

| Risk Identification |  | Qualitative Rating |  |  | Risk Response |  |
| --- | --- | --- | --- | --- | --- | --- |
| Risk | Persons Affected | Probability | Impact | Risk Score | Risk Response | Risk Owner |
| Main entrance open door, access to general public | Students and Teachers | 8 | 8 | 64 | Buzz in system should be implemented |  |
| Uneven paving slabs at entrance | All users | 10 | 5 | 50 | Remove/repair paving |  |
| Access from ex-principles bungalow to main hallway | Students and Teachers | 10 | 5 | 50 | Stud partition erected in hallway |  |
| Boys dorm toilets outdated - damage to flooring | Students | 5 | 5 | 25 | Upgrade toilets |  |
| Vertical slider windows-risk of children falling out | Students | 8 | 10 | 80 | Proper stops to be fitted to windows |  |
| Fire escapes-are not fire escape doors(standard domestic) | Students | 6 | 8 | 48 | Upgrade doors and fit alarms to same |  |
| Loose paint falling from walls and ceilings | Students | 10 | 5 | 50 | Remove all loose paint and repaint walls and ceilings |  |
| Storage heaters displaying burn marks | Students and Teachers | 7 | 8 | 56 | Replace all defective heaters |  |
| Stairways with no handrail (MORPHEOS) | Students | 6 | 8 | 48 | Place handrails to all stairs |  |
| Moulding peeling away from ceiling (boys common room) | Students and Teachers | 6 | 6 | 36 | Repair to damaged moulding |  |
| Pressure release valve for central heating (boys common room) | Students and Teachers | 6 | 9 | 54 | Should be housed off so cannot release pressure to room |  |
| Plywood repairs to floors- trip hazard | Students and Teachers | 8 | 5 | 40 | Repair floors using similar floor boards |  |
| Plastic bags blocking chimneys | Students and Teachers | 5 | 7 | 35 | Use proper method to stop draught |  |
| Loose unterminated cables throughout the building | Students and Teachers | 5 | 10 | 50 | Remove or terminate properly |  |
| Door to Science lab from girls dorm room | Students | 6 | 10 | 60 | Remove access to the lab from girls room |  |
| Door leading from boys shower room to girls dorm | Students | 5 | 9 | 45 | Access to be permanently removed |  |
| Steps at doorways- trip/fall hazard | Students | 9 | 6 | 54 | Signage at a minimum to be in place/handrails |  |
| Goods delivery through hallway to girls dorm not always locked | Students | 7 | 9 | 63 | Review - deliveries to buzz in and be accompanied |  |
| No fire orders displayed | All users | 5 | 10 | 50 | Fire orders to be generated and displayed |  |
| Fire escape from Montessori made of wood and in bad repair | Children and Teachers | 6 | 10 | 60 | To be replaced with metal stairs |  |
| Stables underneath Montessori-no insulation or fire proofing | Children and Teachers | 6 | 10 | 60 | Seal, insulate and fire rated slabs to be fitted |  |
| Plant rooms and switch gear in hallways | All users | 6 | 10 | 60 | Plant rooms and switch gear to be isolated from public |  |
| Open manholes and steel plates covering manholes | All users | 6 | 9 | 54 | Repair all manholes and fit proper covers |  |
| Large amount of extension leads | All users | 5 | 7 | 35 | Upgrade sockets to minimise use of leads |  |
| Gas bottles standing against wall | All users | 5 | 9 | 45 | Gas bottles should be caged off from public |  |
| Incomplete ceilings- slabs missing leaving holes | All users | 5 | 6 | 30 | Repair to all damaged ceilings |  |
| Laundry room to small- removal of items from machines space restricted | Staff | 5 | 7 | 35 | Increase laundry room or relocate |  |
| Oil tanks located too close to building | All users | 6 | 10 | 60 | Relocator bund |  |
| Gas tanks open access | All users | 6 | 8 | 48 | Tanks should be fenced off |  |
| Cricket score shed- in very poor repair | All users | 6 | 7 | 42 | Replace in the new |  |
| Railing around moate alon perimeter of building | All users | 6 | 9 | 54 | Repair and/or replace |  |
| Access to/from golf course near tennis courts | All users | 6 | 8 | 48 | Erect fencing at corner of tennis courts |  |
| Private dwellings with access to grounds - no boundary |  | 6 | 7 | 42 | Define boundaries |  |
| Holes in floors and uneven surfaces |  | 6 | 5 | 30 | repair and make good |  |
| Sleep over rooms for teachers doubling as stores |  | 5 | 6 | 30 | Remove storage material |  |
| Old airplane hanger used as indoor sports facility- in very bad repair not fit for purpose. |  | 6 | 10 | 60 | Repair or replace with new facility |  |
|  |  |  |  | 0 |  |  |
|  |  |  |  | 0 |  |  |

| Key Terms |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| Risk: The risk stated in a complete sentence which states the cause of the risk, the risk, and the effect that the risk causes to the project. |  |  |  |  |  |  |
| Probability: The likelihood that a risk or opportunity will occur (on a scale from 0 to 10 with 10 being the highest). |  |  |  |  |  |  |
| Impact: The impact of the risk on the project if the risk occurs (scale from 0 to 10 with 10 being the highest). |  |  |  |  |  |  |
| Risk Score: Determined by multiplying probability and impact (scale from 0 to 100). |  |  |  |  |  |  |
| Risk Response: The action which is to be taken if this risk occurs. |  |  |  |  |  |  |
| Risk Owner: The person who the project manager assigns to watch for triggers and manage the risk response if the risk occurs. |  |  |  |  |  |  |